## Sheet1
Calculations based on:
Battery bank parameters |  | Value | Comments
Days without sunshine |  | 5 | Days autonmous power without sunshine
Discharge level (e.g. 50%) |  | 0.5 | Assumes maximum desired discharge level
Battery Derate annually at ambient (%) |  | 6.3% | Some compensation for temperature fluctations outside of desired range
Battery voltage |  | 12
Battery Ah |  | 150 | [8 empty] | Dropdown
Panel size (W) |  | 55 | [8 empty] | AC
Sun Hrs (Design Month) |  | 2.1 | See table below for Nova Scotia (enter value for worst case scenario) | [7 empty] | DC
Battery Efficiency |  | 85%
Charge Controller Efficiency |  | 90%
Inverter Efficiency |  | 85% | typical for small inverters
Misc Losses |  | 2% | wire, voltage drop etc.
Appliance | Watts | AC/DC | Hr/day | Daily Wh | Battery Bank (Wh) | Ah | # batteries (rounded up) | # of Panels Needed In December | # of Panels Needed In October | # of Panels Needed In July
notebook | 30 | AC | 24 | 864.3457 | 9224.6077 | 768.7173 | 6 | 10 | 6 | 3
notebook | 20 | AC | 24 | 576.2305 | 6149.7384 | 512.4782 | 4 | 7 | 4 | 2
Bonedoggle (4FCD) | 6.6 | DC | 24 | 161.6327 | 1725.0016 | 143.7501 | 1 | 2 | 1 | 1
Bonedoggle (3FCD) | 5.5 | DC | 24 | 134.6939 | 1437.5014 | 119.7918 | 1 | 2 | 1 | 1
Bonedoggle (2FCD) | 4.5 | DC | 24 | 110.2041 | 1176.1375 | 98.0115 | 1 | 2 | 1 | 1
Bonedoggle (1FCD) | 3.8 | DC | 24 | 93.0612 | 993.1828 | 82.7652 | 1 | 2 | 1 | 1
SRX-DL | 2 | DC | 24 | 48.9796 | 522.7278 | 43.5606 | 1 | 1 | 1 | 1
Nova Scotia
| Sunshine hrs per day HFX | daylight hrs |  | Average WH generated per day per panel | adjusted for CC and battery losses
Jan | 2.9 | 9.5 |  | 159.5 | 122.0175
Feb | 4 | 10.5 |  | 220 | 168.3
March | 4.1 | 12 |  | 225.5 | 172.5075
Apr | 4.5 | 13.5 |  | 247.5 | 189.3375
May | 6.3 | 14.8 |  | 346.5 | 265.0725
Jun | 7.5 | 15.5 |  | 412.5 | 315.5625
Jul | 7.7 | 15.25 |  | 423.5 | 323.9775
Aug | 7.2 | 14 |  | 396 | 302.94
Sep | 5.4 | 12.5 |  | 297 | 227.205
Oct | 4 | 11 |  | 220 | 168.3
Nov | 2.5 | 9.5 |  | 137.5 | 105.1875
Dec | 2.1 | 8.8 |  | 115.5 | 88.3575
This worksheet was developed from resources found on the web and modified with the help of Jonathan Gorham. Thanks!!
http://www.alternative-energy-concepts.com/solar-power.html
Note on A5: Jonathan Gorham: Changed to Battery Derate based on annual ambient temeratures from RETSCREEN for Nova Scotia
Note on A9: Jonathan Gorham: Daylight hours irrelevant, average sunlight hours used for calculation
Note on C14: Jonathan Gorham: Data validated to AC or DC dropdown
Note on E14: Jonathan Gorham: AC Takes inverter efficiency and misc losses into account, DC only takes misc losses into account
The Daily WH calculation now takes into account the effect of the inverter efficiency dependent on whether the load is AC or DC, which is now governed by dropdown. Both take into effect misc losses - which could be the voltage drop based on the length and size of the wires between the panels and charge controller. The Battery Bank Wh calculation has been adjust to take the annual battery temperature derate coefficient into account, which is taken from the RETScreen estimate for that value for Sable Island weather data. Number of batteries has been rounded up (although if you find partial batteries, let me know). The number of panels needed is based on the December average sunlight hours, and the resultant expected daily harvest per module, taking into account the charge controller losses.